## Sheet1
Domain | SRI Code(s) | Service Name | Equipment Category | Manufacturer | Model | Func. Level Achieved (0-4) | Official Level Definition (SRI v4.5) | Typical Price | Key Technical Specs | Required Interface / Protocol | Companion Components Needed | How Equipment Achieves This Level | Source Link (verify) | Notes | Typical Price (EUR) [converted/verified]
Cooling | C-1a | Cooling emission control | Smart TRV / room controller (dual heat-cool) | Danfoss | Ally TRV (used on 2-pipe fan-coil or radiator cooling) | 2 - 3 | Individual room control / with communication to BACS | £55 - £65 / unit | Same as H-1a Ally TRV; usable on reversible 2-pipe systems | Zigbee → Danfoss Ally Gateway | Danfoss Ally Gateway / Zigbee-BACnet bridge | Same mechanism as heating: individual room setpoint + Zigbee communication to a gateway bridged into BACS - Level 3. | https://www.danfoss.com/en-gb/products/dhs/smart-heating/smart-heating/danfoss-ally/ |  | €64.23 - €75.91 (conv. from £)
Cooling | C-2a | Generator control for cooling | VRF/VRV outdoor unit + central controller | Daikin | VRV system + Intelligent Touch Manager (iTM) | 2 - 3 | Variable control of cooling capacity depending on load (L2) / + external grid signal (L3) | iTM controller: POR (typ. €3,000 - €6,000); VRV outdoor units priced per project | Inverter compressor(s), central BACnet/LonWorks gateway (DMS504B71), demand control | BACnet MS/TP or LonWorks via Daikin DIII-NET gateway | Daikin DIII-NET → BACnet/LonWorks Interface (DMS504B71) for BMS integration | Inverter-driven variable-capacity compressors satisfy load-based control (L2); adding the BACnet gateway lets a BMS/DR signal from the grid modulate capacity, reaching L3. | https://www.daikin.eu/en_us/products/intelligent-touch-manager.html |  | €3,000 - €6,000
Cooling | C-2a | Generator control for cooling | VRF system + central controller | Mitsubishi Electric | City Multi + AE-200E/AG-150A controller | 2 - 3 | Variable control depending on load (L2) / + external signals (L3) | AE-200E controller: POR (typ. €2,500 - €5,000) | Inverter compressors, BACnet/LonWorks/Modbus gateway options, scheduling, energy reporting | BACnet IP/MS-TP, LonWorks, or Modbus via AE-200E gateway | AE-200E/AG-150A central controller for demand control & BMS linkage | Central controller exposes load-based variable capacity control and, once linked to grid/DR signals via BACnet, satisfies the L3 definition of C-2a. | https://www.mitsubishielectric.co.jp/ldg/ihp/global/products/vrf/en/controller/ |  | €2,500 - €5,000
Cooling | C-3 | Report cooling system performance | Cooling energy sub-metering | Siemens / Kamstrup | Cooling energy meter + wireless M-Bus | 1 - 2 | Current KPIs (L1) / + historical data (L2) | €150 - €350 per meter | Ultrasonic flow + matched temperature sensor pair, M-Bus/Modbus output | M-Bus/Modbus → BMS gateway | M-Bus collector | Meters cooling energy at plant or zone level for KPI reporting; history logging via the gateway/BMS reaches L2. | https://www.kamstrup.com/en-en/heat-solutions/heat-meters |  | €150 - €350
Cooling | C-2a / C-2b | Cooling generator control + sequencing (central plant) | Air-cooled packaged chiller | Carrier | AquaSnap 30RC (10-60 ton) / AquaForce 30XV (variable-speed) | 2 - 3 | L2 variable control based on load/demand (Greenspeed inverter) / L3 with external grid/DR signal via BACnet EMM | Est. $700 - $1,500/ton for <150-ton air-cooled units (industry benchmark) → a 30-ton 30RC unit ≈ $25,000 - $40,000 | Greenspeed Intelligence variable-speed scroll compressors, microchannel condenser coils, PIC6 control interface, EER up to 10.9, IPLV up to 19.0 | Native BACnet® communication (factory option) or BACnet+LON translator (field accessory); Energy Management Module (EMM) for external 4-20mA demand-limit signal | Energy Management Module (EMM) for grid/DR signal reception; ChillerVisor or Touch Pilot display for local supervision | Greenspeed variable-speed compressors continuously match capacity to load (C-2a L2); the EMM accessory accepts an external demand-limit or utility DR signal, which is what elevates control to 'variable control based on load AND external signals from grid' (L3). | https://www.carrier.com/commercial/en/us/products/chillers-components/air-cooled-chillers/30rc/ | Price is a market benchmark (cost-per-ton across multiple independent sources), not a specific Carrier quote - chillers are always quoted per-project. The $/ton figure is far more reliable for this equipment class than a fixed dollar range. | €607.76 - €1,302 (conv. from $)
Cooling | C-2a / C-2b | Cooling generator control + sequencing (large central plant) | Air-cooled inverter screw chiller | Daikin | EWAD-TZ (170-710 kW) | 2 - 3 | L2 variable control based on load (inverter-per-compressor) / L3 with external 4-20mA demand-limit or BACnet network override | Est. $450 - $700/ton for 150+ ton systems (industry benchmark, converts to roughly $22,000 - $140,000 for the 170 - 710kW range) | Each compressor individually inverter-driven with self-monitoring, dual leaving-water-temperature setpoints, native BACnet BTL-certified over IP and MS/TP | BACnet BTL-certified (native) or LonWorks/Modbus optional; capacity can be overridden by external 4-20mA signal or network command | Building BMS with 4-20mA output or BACnet network override capability to exercise the demand-limit function | Per-compressor inverters give genuinely load-proportional capacity control; the documented ability to demand-limit capacity via an external 4-20mA signal or network command directly satisfies the 'external signals from grid' element of C-2a/C-2b Level 3. | https://www.daikin-ce.com/content/dam/document-library/operation-manuals/as/EWAD-TZ_EWAD-TZB_EWWD-VZ_D-EOMZC00105-17_Operation%20manuals_English.pdf | Price is a market benchmark, not a Daikin quote - same caveat as the Carrier chiller above | €390.70 - €607.76 (conv. from $)
Cooling | C-1a | Cooling emission control (fan coil, room level) | Fan coil unit with electronic wired controller | Daikin | FWC-BT/BF (2-pipe/4-pipe) + FWEC2T/4T controller | 1 - 2 | L1 central automatic control (fixed setpoint) / L2 individual room control via wired FWEC controller | FCU: est. €600 - €2,800 depending on capacity/pipe config; FWEC controller: est. €80 - €180 (not independently price-confirmed - no public Daikin EU price list found) | BLDC fan motor option (up to 70% fan-energy saving vs AC motor), 2-pipe/4-pipe/BLDC controller variants, Modbus integration into BMS | FWEC controller: on/off valve + Modbus (via optional gateway) for BMS integration | Modbus gateway for BMS-level visibility/control if not using the standalone wired controller | The FWEC wired controller gives each fan coil independent room-level temperature control (L1 - L2); reaching L3 ('communication to BACS') requires the Modbus BMS integration option, which is available but not standard. | https://general-catalogue.daikin.eu/flipbooks/EN/General_catalogue/11fcu/index.html | Price NOT independently confirmed against a distributor - flagged as catalogue-spec-only; treat range as indicative until a specific quote is obtained | €600 - €2,800
Domestic hot water | DHW-1a | Control of DHW storage charging (electric) | Smart electric hot water cylinder | Mixergy | Mixergy Smart Hot Water Cylinder | 3 | Automatic charging control based on local availability of renewables or grid information (DR/DSM) | £1,300 - £1,800 (cylinder, size dependent) | Multi-sensor stratification measurement, immersion + coil, app control, Octopus Agile/solar-surplus integration | Wi-Fi → Mixergy Cloud API; integrates with Octopus Energy Agile tariff & solar inverters | Smart meter / solar inverter API link for renewable-availability signal | Multi-sensor tank state + cloud API lets a HEMS charge the tank preferentially during cheap-rate or solar-surplus periods - directly matches the Level 3 definition. | https://www.mixergy.co.uk/how-it-works/ |  | €1,518 - €2,102 (conv. from £)
Domestic hot water | DHW-1b | Control of DHW storage charging (non-electric / heat source) | Smart cylinder controller (heat-pump/boiler fed) | Viessmann | Vitocell + Vitotronic 200 control | 2 - 3 | L2: scheduled charging enable / L3: demand-based supply temp + multi-sensor management | Cylinder €1,200 - €2,500; Vitotronic control typically bundled with the heat source | Multiple immersion sensors, ViCare app, integrates with Vitocal heat pumps / Vitodens boilers | Vitonet / OptoLink → ViCare cloud; KNX/Modbus gateway available for BMS | Vitocomfort/BACnet gateway for building-level integration | Vitotronic's layered tank sensors + scheduling deliver demand-based charging and multi-sensor management, matching Level 3 when linked to the heat generator's demand logic. | https://www.viessmann.co.uk/en/products/hot-water-cylinders.html |  | €1,200 - €2,500
Domestic hot water | DHW-1d | DHW storage with solar collector | Solar thermal controller | RESOL | DeltaSol BS/4 Plus | 2 - 3 | Automatic solar + supplementary storage charge, demand-oriented / multi-sensor management | €239 - €443 (DeltaSol BS Plus bundle ~€240; BX Plus controller-only ~€443) | Multiple PT1000 sensors, VBus data logging, RESOL VBus/LAN for remote monitoring | RESOL VBus → DL3/DL2 datalogger → cloud/BMS | DL3 VBus/LAN data logger for BACS/BMS visibility | Prioritises solar-loop charging over auxiliary heat source and manages multiple sensors in the tank - matches L2/L3 definitions depending on whether return-temperature control is also configured. | https://www.resol.de/en/produktdetail/deltasol-bs-4-plus |  | €239 - €443
Domestic hot water | DHW-3 | Report information regarding DHW performance | DHW sub-metering & reporting | Kamstrup / Techem | Heat/water meter + wireless M-Bus (shared with H-3 metering infrastructure) | 1 - 2 | Indication of actual values / actual values + historical data | €80 - €250 per meter | Ultrasonic/ ultrasonic ready ,wireless M-Bus, ~10 - 16 yr battery | Wireless M-Bus → gateway → BMS/portal | M-Bus collector + tenant portal / BMS dashboard | Provides submetered DHW energy/volume with historical logging - matches L1/L2 depending on whether a reporting dashboard with history is deployed. | https://www.kamstrup.com/en-en/heat-solutions/heat-meters |  | €80 - €250
Dynamic building envelope | DE-1 | Window solar shading control | Motorised blind/shade motor + smart hub | Somfy | Sonesse 30 WireFree RTS motor + TaHoma Switch hub | 2 - 3 | Motorised operation with automatic control based on sensor data (L2) / combined light/blind/HVAC control (L3) | Motor ~$150 - - $300 per blind; TaHoma Switch hub ~$130 - $180 | RTS radio motor, quiet operation, TaHoma hub adds Wi-Fi/scene/weather-based automation, IFTTT/Alexa/Google integration | Somfy RTS radio → TaHoma Switch (Wi-Fi) → cloud API / IFTTT / KNX gateway | Somfy Eolis 3D wind sensor (safety retraction); sun/light sensor for full automatic operation | Motorised + sensor-triggered (sun/wind) operation matches L2; linking TaHoma scenes to the HVAC/lighting system (e.g. close blinds when cooling setpoint is being fought) reaches L3 'combined light/blind/HVAC control'. | https://www.somfysystems.com/en-us/products/shades-blinds-curtains/motorized-blinds-shades |  | €130.23 - €260.47 (conv. from $)
Dynamic building envelope | DE-1 | Wind safety sensor for shading | Wireless wind sensor | Somfy | Eolis 3D WireFree RTS | - | Enabling component (not itself a functionality level) | $239.95 (unit) | Battery-powered 3-axis wind sensor, automatic retraction on high wind, RTS radio | Somfy RTS → motor/hub | Required alongside the shading motor for safe automatic operation | Provides the wind-triggered automatic retraction signal that is a precondition for unattended (L2+) automatic shading operation. | https://www.walmart.com/browse/electronics/somfy/3944/YnJhbmQ6U29tZnkie |  | €208.33 (conv. from $)
Dynamic building envelope | DE-2 | Window open/closed control combined with HVAC | Window contact + HVAC interlock | Various (e.g. Fibaro / KNX window contacts) | Door/Window sensor + KNX/Zigbee binary input | 1 - 2 | Open/closed detection to shut down heating/cooling (L1) / + automised mechanical window opening (L2) | $25 - $60 per contact sensor | Reed switch/magnetic contact, Zigbee/Z-Wave/KNX output | Zigbee/Z-Wave/KNX → BMS/HEMS logic to interlock HVAC | BMS/HEMS automation rule to pause heating/cooling on window-open event | Detects window state and, wired into the BMS interlock logic, shuts down local heating/cooling when open - matches Level 1; motorised opening (L2) needs an actuated window/vent, not just a contact sensor. | https://www.knx.org/knx-en/for-professionals/index.php | Generic KNX/Zigbee category - verify a specific certified product with your integrator | €21.71 - €52.09 (conv. from $)
Dynamic building envelope | DE-4 | Reporting on dynamic envelope performance | Blind position + fault reporting via smart hub | Somfy | TaHoma Switch (cloud reporting) | 1 - 2 | Position of each product & fault detection (L1) / + predictive maintenance (L2) | Included with TaHoma Switch hub (~$130 - $180) | Cloud logging of motor position, obstacle-detection fault codes, app history | Wi-Fi → Somfy Cloud → 3rd-party API/BMS | - | TaHoma logs each motor's position and communicates jam/obstacle faults to the app - satisfies L1; true predictive maintenance (L2) requires analytics on top of the raw fault log, which TaHoma does not natively provide. | https://www.somfysystems.com/en-us/products/smart-home-controls/smart-home |  | €112.87 - €156.28 (conv. from $)
Dynamic building envelope | DE-1 / DE-2 | Window solar shading + open/closed control (KNX-native) | KNX shading/blind actuator | ABB | i-bus KNX Shutter/Blind Actuator (SA/S series) | 2 - 3 | L2 motorised operation with automatic control based on sensor data / L3 combined light/blind/HVAC control via KNX group addressing | Est. €150 - €400 per multi-channel actuator (not independently confirmed against a distributor quote) | DIN-rail KNX actuator, multiple blind/shutter channels, travel-time calibration, integrates with any KNX sun/wind sensor | KNX TP (native) - no gateway needed within a KNX installation | KNX weather station (sun/wind sensor) for automatic operation; KNX visualisation/logic for combined light/blind/HVAC scenes | Because it's KNX-native, this actuator can be grouped in the same KNX project as lighting (L-1a/L-2) and HVAC interlocks (via a KNX binary output), making 'combined light/blind/HVAC control' (DE-1 L3) a matter of ETS programming rather than a separate integration project - a genuine advantage over RTS-based systems (Somfy) that need a gateway to reach the same result. | https://www.abb.com | Price not independently confirmed against a distributor quote. Included as a KNX-native alternative to the Somfy/Lutron shading entries already in this database, relevant where the rest of the building is KNX-based | €150 - €400
Electric vehicle charging | EV-15 | EV charging capacity | Smart AC wallbox (single point) | Zaptec | Zaptec Go 2 | 3 - 4 | 10 - 50% of parking spaces covered (L3) / >50% covered (L4) - level depends on site-wide coverage, not the unit itself | €629 - €638 (unit) + €400 - €600 installation | 7.4kW single-phase / 22kW three-phase auto-switching, MID-certified meter, 4G (no home Wi-Fi dependency), 3.2kg | 4G/Wi-Fi → Zaptec Cloud; OCPP support for CPO/BMS integration | Zaptec Sense for dynamic load balancing across multiple chargers | Coverage-based level (EV-15) is a site-wide metric; each Go 2 unit contributes one covered parking space toward the 10-50% / >50% thresholds used in the SRI calculation. | https://teslacharger.co.uk/chargers/zaptec-go-2/ |  | €629 - €638
Electric vehicle charging | EV-16 | EV Charging Grid balancing | Solar-matching / smart-charging wallbox | myenergi | Zappi V2.1 | 1 | 1-way controlled charging (desired departure time + grid/solar signals for optimisation) | €829 (unit) | ECO+ solar-surplus charging mode, integrates with myenergi Eddi (water heating) and Libbi (battery), app scheduling | myenergi Hub (Wi-Fi/GSM) → myenergi app/API | myenergi Harvi wireless CT sensor (reads solar/grid import in real time) | ECO+ mode continuously throttles charge current to match solar surplus and lets the driver set a required-by time - the literal definition of 1-way controlled (Level 1) charging. | https://www.wallboxdiscounter.com/en/ev-charger/zappi/ |  | 829
Electric vehicle charging | EV-16 / EV-17 | Bi-directional charging + connectivity | Bidirectional (V2G/V2H) DC wallbox | Wallbox | Quasar 2 | 2 | 2-way controlled charging (V2G/V2H) with desired departure time and grid signals | ~€3,000 - €4,000 (unit; requires compatible EV) | CHAdeMO bidirectional DC, 7kW export/import, works with V2G-capable EVs (e.g. Nissan Leaf, some Renault models) | myWallbox app/API; local CHAdeMO V2G protocol to vehicle | V2G-compatible electric vehicle; export agreement with DNO/utility | Physically capable of pushing stored EV energy back to the home/grid on schedule - the literal Level 2 'bi-directional charging' definition, contingent on vehicle compatibility. | https://www.wallboxdiscounter.com/en/ev-charger/bidirectional-ev-charger/ |  | €3,000 - €4,000
Electric vehicle charging | EV-17 | EV charging information and connectivity | ISO 15118 Plug&Charge-capable charger | Zaptec | Go 2 (ISO 15118-20 hardware-ready) | 2 | Reporting to occupant + automatic driver ID/auth (ISO 15118 compliant) | €629 - €638 | V2G-ready hardware per ISO 15118-20; MID meter for accurate billing; app status reporting | PLC (ISO 15118) over the charge cable to the vehicle; app for occupant reporting | Vehicle with matching ISO 15118-20 support for full Plug&Charge | Reports charging status to the occupant via the app and, with a compliant vehicle, performs automatic Plug&Charge identification/authorisation - matching Level 2. (Vendor note: full V2G registration currently requires additional certified system components in some markets.) | https://jointcharging.com/glossary/iso-15118/ |  | €629 - €638
Electric vehicle charging | EV-15 / EV-16 / E-3 | Solar-optimised EV charging + storage interaction | AC Wallbox with PV surplus-charging integration | KOSTAL | ENECTOR AC Wallbox 3.7/11 kW | EV-15: 3 - 4 (coverage-dependent) / EV-16: 1 (1-way solar/grid-aware charging) / E-3: 2 (grid-signal-aware storage interaction) | EV-16 L1: 1-way controlled charging including desired departure time and grid/solar signals for optimisation | €598.77 incl. 19% VAT (€503.17 excl. VAT) | 3.7kW (1-phase) / 11kW (3-phase), up to 16A/phase, IP54, integrated DC residual-current monitoring, 7.5m Type 2 cable, Solar Pure / Solar Plus / Power / Time charging modes | Communicates with KOSTAL PLENTICORE plus hybrid inverter + KOSTAL Smart Energy Meter over KOSTAL's proprietary energy-management protocol | KOSTAL Smart Energy Meter (required for Solar Pure/Plus modes) + PLENTICORE plus inverter for full PV/battery-aware charging | Solar Plus' mode throttles charge current in real time to minimise grid draw, factoring in connected battery storage - directly implementing EV-16's 'controlled charging including... grid signals for optimisation' and contributing to E-3's 'controller optimising the use of locally generated electricity'. | https://www.elektromax24.de/kostal-wallbox-enector-3.7-11 | Cross-check vs user-supplied sheet: user's €2,756 is ~4.6x the confirmed €598.77 retail unit price - likely includes installation, the required KOSTAL Smart Energy Meter, and/or a PLENTICORE inverter bundle. Flagging as a probable installed-system total, not the wallbox unit price. | 598.77
Electricity | E-3 | Storage of locally generated electricity | Home battery + hybrid inverter | Tesla | Powerwall 3 | 3 - 4 | On-site storage with controller optimising self-consumption (L3) / + feed-back to grid (L4, region dependent) | $9,300 - $10,500 (unit); $13,000 - $16,500 installed | 13.5 kWh usable (LFP), 11.5 kW continuous power, integrated solar inverter, Storm Watch, stackable to 4 units (54 kWh) | Tesla Gateway → Tesla app/API; supports OCPP-adjacent utility DR programs in some markets | Tesla Gateway (included); utility/DR program enrolment for export/DSM participation (L4) | Built-in optimisation self-consumes solar preferentially and can be scheduled around tariffs - Level 3; enrolling in a utility virtual power plant / export programme realises Level 4 'possibility to feed back into the grid'. | https://www.energysage.com/energy-storage/best-home-batteries/tesla-powerwall-battery-complete-review/ |  | €8,075 - €9,116 (conv. from $)
Electricity | E-3 | Storage of locally generated electricity | Modular home battery | BYD | Battery-Box Premium HVS | 2 - 3 | On-site storage with grid-signal controller (L2) / optimising self-consumption (L3) | €4,000 - €8,000 (5 - 20 kWh modular) | Modular stackable LFP blocks, works with 3rd-party hybrid inverters (SMA, Fronius, Goodwe, etc.) | CAN bus to inverter; inverter's own cloud/Modbus for BMS integration | Compatible hybrid inverter (SMA Sunny Boy Storage, Fronius GEN24, etc.) | Inverter-managed self-consumption optimisation achieves L3 when paired with an inverter offering PV-forecast-based charging logic; without that, base grid-signal charging is L2. | https://www.surgepv.com/blog/tesla-powerwall-vs-byd-vs-sonnen |  | €4,000 - €8,000
Electricity | E-4 | Optimising self-consumption of locally generated electricity | Home Energy Management System (HEMS) | gridX / Tibber | gridXOS HEMS / Tibber Pulse + app | 2 - 3 | Automated management based on current renewable availability (L2) / + predicted needs & availability (L3) | Tibber Pulse hardware ~€99 + subscription; gridX POR (B2B platform, typically licensed per install) | Real-time meter reading, dynamic tariff integration, forecast-based load shifting (EV, heat pump, battery) | Smart meter pulse output → HEMS cloud → device APIs (SG-Ready, OCPP, Modbus) | Smart meter with pulse/S0 output or direct utility API access | Combines live production/consumption data with day-ahead price/weather forecasts to pre-emptively shift heat-pump, battery and EV charging - the literal L3 definition of E-4. | https://www.gridx.ai/knowledge/sg-ready |  | 99
Electricity | E-2 / E-11 / E-12 | Reporting on generation / storage / consumption | Smart energy meter / CT clamp monitor | Shelly | Shelly Pro 3EM (3-phase energy meter) | 2 - 3 | Actual values + historical data (L2) / performance evaluation incl. forecasting (L3, via 3rd-party analytics) | €70 - €90 (Shelly official store); ~$155 / ~€140 on Amazon US (import/reseller pricing) | 3-phase CT-clamp metering, Wi-Fi, local + cloud API, DIN-rail mount | Wi-Fi → Shelly Cloud / local HTTP-Modbus API → BMS or HEMS | Home Assistant / HEMS platform for forecasting-grade reporting | Provides real-time and logged historical generation/consumption data per phase; feeding this into a HEMS/BMS analytics layer with forecasting satisfies the higher reporting levels. | https://www.shelly.com/en/products/shelly-pro-3em |  | €70 - €90
Electricity | E-2 | Reporting on local electricity generation (PV) | Monocrystalline N-type PV module | Trina Solar | Vertex S+ NEG9RC.27 (425-710W, up to 22.5% efficiency) | 1 - 2 (module itself contributes to generation; reporting level depends on inverter/monitoring platform) | Generation data availability depends on the paired inverter/monitoring system, not the panel itself | $0.45 - $0.95/W (2026 US retail benchmark) → a 425W panel ≈ $190 - $400; EU wholesale pricing tends toward the lower end (≈€0.30 - €0.50/W) | N-type i-TOPCon cells, bifacial option, 25-year product / 25-year 87.4% power warranty | The panel itself has no data interface - generation reporting (E-2) is delivered entirely by the paired inverter's monitoring platform (e.g. SolarEdge, Fronius, Huawei) | A compatible string/hybrid inverter with cloud monitoring (e.g. SolarEdge, Fronius Solar.web) is REQUIRED to realise any E-2 functionality - the panel alone cannot | PV modules have no role in the SRI's E-2 reporting service beyond generating the energy that gets measured; the functionality level is entirely determined by the inverter/monitoring layer, not the panel choice. Included here for completeness of a PV system BOQ, not because the panel itself drives the SRI score. | https://solartechonline.com/blog/trina-solar-panel-prices-2025-guide/ | Important: don't let a PV panel line item imply SRI credit on its own - E-2/E-3/E-4 credit comes from the inverter and its control/reporting capability, covered separately in this database (see Tesla Powerwall/BYD/gridX rows) | €0.39 - €0.82 (conv. from $)
Electricity | E-3 | Storage of locally generated electricity | DC-coupled home battery (higher capacity) | LG Energy Solution | RESU16H Prime (16 kWh, 400V) | 2 - 3 | L2 storage with grid-signal controller / L3 storage with controller optimising local renewable use (via paired hybrid inverter's EMS) | $11,000 - $16,000 installed (US); equipment-only typically ≈$2,000 - $4,000 less than the RESU10H Prime tier | 16 kWh usable capacity, 400V DC-coupled (requires compatible hybrid inverter e.g. SolarEdge StorEdge), 94.5 - 97.5% round-trip efficiency, NMC chemistry, 6,000+ cycles to 80% retention | DC-coupled to a compatible hybrid inverter (SolarEdge, etc.) - the inverter's EMS provides the actual grid-signal/optimisation logic, not the battery itself | Compatible hybrid inverter (e.g. SolarEdge StorEdge) required - RESU is not a standalone AC-coupled retrofit battery | As with the PV module above, the battery hardware provides the storage medium but the SRI-relevant control logic (grid-signal response, self-consumption optimisation) lives in the paired inverter/EMS. Its high round-trip efficiency (DC-coupled, single inversion) is a genuine technical advantage over AC-coupled alternatives for E-3/E-4 purposes. | https://solartechonline.com/blog/lg-resu-battery-guide/ | Cross-check vs 2nd user sheet: sheet's €12,000 - €14,500 sits within the confirmed $11,000 - $16,000 US installed range once converted - plausible | €9,551 - €13,892 (conv. from $)
Heating | H-1a | Heat emission control | Smart TRV (electronic radiator valve) | Danfoss | Ally TRV (014G24xx, Zigbee) | 3 | Individual room control with communication between controllers and to BACS | £55 - £65 / unit | Zigbee 2.4GHz, M30x1.5 + RA/RAV/RAVL adapters, 1.2W, battery powered | Zigbee → Danfoss Ally Gateway (or 3rd-party Zigbee hub) | Danfoss Ally Gateway (or Home Assistant/SmartThings Zigbee coordinator) to expose data to a BACS/EMS | Individually meters and sets each room's temperature and reports status over Zigbee to a gateway that can be bridged into a BMS - satisfies 'communication between controllers and to BACS'. Level 4 (occupancy detection) needs an added occupancy sensor/ecosystem integration, which Ally alone does not provide. | https://www.danfoss.com/en-gb/products/dhs/smart-heating/smart-heating/danfoss-ally/ | Level 4 requires pairing with an occupancy-aware ecosystem (e.g. via Home Assistant automations) | €64.23 - €75.91 (conv. from £)
Heating | H-1a | Heat emission control | Smart TRV | tado° | Smart Radiator Thermostat X | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) | £87 - £105 / unit (Starter Kit w/ Bridge X ~£214) | M30x1.5 + adapters for Danfoss RA/RAV/Comap/Herz, open-window detection, geofencing | tado° proprietary RF → tado° Internet Bridge (needed for remote/BACS access) | tado° Internet Bridge; API integration for BACS bridging | Provides individual room control via the app; reaches Level 3 only once bridged to the tado° API/BACS - standalone (bridge-less) it is Level 2. | https://support.tado.com/en/articles/3482335 |  | €101.60 - €122.63 (conv. from £)
Heating | H-1a | Heat emission control (basic/central) | Smart room thermostat | Google | Nest Learning Thermostat (4th gen) | 1 - 2 | Central automatic control (L1) / Individual room control (L2, with room sensors) | $230 (4th gen bundled w/ 1 Temp Sensor); additional Temp Sensor (2nd gen) ~$40 each | Radar-based occupancy, Wi-Fi, learns schedule, multi-room sensors optional | Wi-Fi → Google Home cloud; Nest API for 3rd-party BACS integration | Additional Nest Temperature Sensors per room for individual-room control | Base unit gives central automatic control (L1); adding per-room Nest Temperature Sensors moves toward individual room control (L2). Occupancy sensing exists but is not exposed as an SRI-grade communicating BACS interface, so it does not reach L3/L4 without a certified gateway. | https://www.consumerreports.org/appliances/thermostats/best-smart-thermostats-of-the-year-a4768074255/ |  | €199.69 (conv. from $)
Heating | H-1a | Heat emission control | Smart thermostat (budget/entry) | Honeywell Home (Resideo) | T6R / X2S Wi-Fi Thermostat | 1 | Central automatic control (e.g. central thermostat) | ~$50 - $95 | Wi-Fi, app scheduling, geofencing (X2S entry model) | Wi-Fi → Resideo/Honeywell Home app | - | Simple central automatic on/off + schedule control of the whole dwelling - matches Level 1 exactly; no per-room control. | https://www.reviewed.com/smarthome/best-right-now/the-best-smart-thermostats | Good low-cost baseline device for Method A assessments | €43.41 - €82.48 (conv. from $)
Heating | H-1c | Control of distribution fluid temperature | Weather-compensation / heating-curve controller | Danfoss | ECL Comfort 310 | 1 - 2 | L1: outside temp. compensated control / L2: demand-based control | POR (typically €250 - €450) | Outdoor sensor + flow/return sensors, PID control of mixing valve & pump, Modbus/M-bus option card | Modbus RTU (via ECA 61/63 accessory) or standalone | Outdoor temperature sensor; Modbus module for BACS integration | Continuously adjusts flow temperature to outdoor conditions (L1); with demand feedback from room units becomes demand-based (L2). | https://www.danfoss.com/en-gb/products/dhs/district-energy/controllers/ecl-comfort/ |  | €250 - €450
Heating | H-1d | Control of distribution pumps in networks | Variable-speed circulation pump | Grundfos | MAGNA3 (25-100 to 65-150 range) | 3 | Variable speed pump control (pump unit internal estimations) | POR (typically €250 - €450) | AUTOADAPT self-learning proportional-pressure control, integrated FC, Grundfos GO Remote (Bluetooth), optional CIM Modbus/BACnet module | Bluetooth (commissioning); CIM module for Modbus/BACnet/LonWorks | Grundfos CIM 150/200/500 fieldbus communication module for external demand-signal control | Internal AUTOADAPT sensorless flow estimation gives Level 3 out of the box; adding an external CIM communication module and demand signal from the BMS raises it to Level 4. | https://www.grundfos.com/products/find-product/magna3 |  | €550 - €1,450
Heating | H-2a / H-2b | Heat generator control | Heat pump with SG-Ready smart-grid interface | Mitsubishi Electric | Ecodan (FTC6 controller) | 2 - 3 | L2: multi-stage/variable capacity control depending on load / L3 with grid signal: variable control depending on load AND external signals from grid | Heat pump unit €6,000 - €12,000 installed; FTC6 controller included | Inverter-driven ASHP, weather compensation, SG-Ready 4-mode potential-free contact input | SG-Ready volt-free relay input (2-bit) from HEMS/smart meter; MELCloud for remote/API access | SG-Ready compatible HEMS relay/controller (e.g. utility DSM box) to actually drive the 4 modes | Inverter modulation gives variable-capacity control (H-2b L2); wiring the SG-Ready contacts to a grid/tariff signal (HEMS) achieves H-4/H-2b L3 'variable control depending on load AND external signals from grid'. | https://les.mitsubishielectric.co.uk/products/heat-pumps/ecodan | SG-Ready is a 2-bit (4-mode) interface - see gridX/BWP explainer link in H-4 row | €6,000 - €12,000
Heating | H-2b | Heat generator control (heat pumps) | Heat pump with grid-reactive controls | Vaillant | aroTHERM plus + sensoHOME / myVAILLANT | 2 - 3 | Variable control depending on load / + external grid signals | €7,000 - €14,000 installed (unit dependent) | Inverter ASHP, SG-Ready, eBUS communication bus, myVAILLANT app/API | eBUS (Vaillant proprietary) + SG-Ready relay; myVAILLANT cloud API | eBUS-Modbus/BACnet gateway for 3rd-party BMS integration | eBUS gives full read/write access to compressor modulation for demand-based control; SG-Ready contact plus myVAILLANT tariff integration provides the external-grid-signal pathway needed for Level 3. | https://www.vaillant.co.uk/products/arotherm-plus/ |  | €7,000 - €14,000
Heating | H-3 | Report information regarding heating system performance | Heat metering / sub-metering + reporting | Kamstrup | MULTICAL 403 heat meter + wireless M-Bus | 2 - 3 | L2: current KPIs + historical data / L3: forecasting/benchmarking (needs analytics layer) | €150 - €300 per meter (POR, distributor dependent) | Ultrasonic heat meter, wireless M-Bus 868MHz, 16-year battery | Wireless M-Bus → M-Bus/Modbus/BACnet gateway into BMS or cloud analytics platform | M-Bus collector/gateway (e.g. Kamstrup READy) + analytics dashboard for forecasting/benchmarking | Meter alone gives current + historical KPI reporting (L2); pairing with an analytics/benchmarking platform (e.g. building energy management software) that forecasts and flags anomalies reaches L3/L4. | https://www.kamstrup.com/en-en/heat-solutions/heat-meters/multical-403 |  | €150 - €300
Heating | H-4 | Flexibility and grid interaction | Smart-grid relay / DSM interface module | Homematic IP / generic HEMS vendors | SG-Ready relay module (e.g. Homematic IP Wired SG-Ready actuator) | 3 | Heating system capable of flexible control through grid signals (e.g. DSM) | €40 - €120 per relay module | 2x potential-free relay outputs mapped to SG-Ready 4-mode logic, KNX/Zigbee/proprietary bus | SG-Ready 2-bit interface into heat-pump controller; KNX/Zigbee back to HEMS | HEMS/EMS software issuing the DSM signal (e.g. based on dynamic tariff or PV surplus) | Physically implements the SG-Ready contract, letting an external HEMS force the heat pump into 'blocked / normal / boost / max' modes in response to grid signals - the literal definition of H-4 Level 3. | https://www.gridx.ai/knowledge/sg-ready | Level 4 (model-predictive control using local + grid predictions) requires a HEMS with forecasting, e.g. gridX, tibber Pulse, or a BMS optimisation layer | €40 - €120
Heating | H-1a / MC-9 | Heat emission control + occupancy detection to connected TBS | Smart thermostat with remote room sensors | Honeywell Home (Resideo) | T9 Smart Thermostat with Smart Room Sensor | 1 - 2 | L1 central automatic control / L2 individual room control via averaging across room sensors | $149.99 (thermostat only) / $175.00 (with 1 Smart Room Sensor, confirmed Amazon US); additional sensors sold separately | 900MHz proprietary wireless room sensors (temp+occupancy), C-wire required (adapter included), Alexa/Google/SmartThings/Apple Home | Wi-Fi → Resideo cloud; no native BACnet - 3rd-party integration via IFTTT/SmartThings only | Additional Smart Room Sensors per room; SmartThings/Home Assistant bridge for any BACS-level exposure | Averages/prioritises temperature across multiple room sensors based on detected occupancy - functionally close to individual-room control (L2), though it lacks a certified BACnet/KNX interface, so it cannot reach L3 ('communication to BACS') without a 3rd-party bridge. | https://www.resideo.com/us/en/products/air/thermostats/wifi-thermostats/t9-smart-thermostat-and-sensor-with-c-wire-adaptor-smhom9610kit/ | Cross-check vs user-supplied sheet: user priced this at €321 for C-1a/C-3/MC-9 mapping - plausible EU retail+VAT, but is a materially different service mapping (cooling, not heating) from what the product is designed for (it's a heating/cooling dual thermostat, so both mappings are defensible) | €130.23 (conv. from $)
Heating | H-3 / H-4 / MC-4 / MC-9 | Reporting, flexibility, fault detection, occupancy | Smart thermostat, ecosystem-integrated | ecobee | SmartThermostat Premium (with voice control + air quality monitor) | 1 - 2 | H-3 L1 - L2 current+historical KPI reporting / MC-9 L1 - 2 occupancy feeding multiple TBS | $249.99 - $279.99 (varies by retailer); SmartSensor 2-pack $99.99 | Built-in occupancy (radar+PIR) sensor, indoor air quality/VOC sensor, multi-room SmartSensors, Alexa built-in, ecobee API | Wi-Fi → ecobee cloud API (documented, 3rd-party developer access) → can be bridged to Home Assistant/BACnet gateways | Additional SmartSensors for multi-room occupancy; Home Assistant/3rd-party bridge for BACS-grade MC-4/MC-9 exposure | ecobee's documented public API is more open than Nest/Honeywell, making it the more realistic path to a genuine H-4 (grid-signal) and MC-9 (cross-TBS occupancy) integration via a HEMS/BACS bridge, though out-of-the-box it only reaches L1 - L2 on these services without that bridge. | https://www.consumerreports.org/appliances/thermostats/best-smart-thermostats-of-the-year-a4768074255/ | Cross-check vs user-supplied sheet: user priced at €394, consistent with EU RRP (~£279/€320 - 350 range); the H-4 Level 2 - 3 claim in the user's sheet requires the HEMS bridge noted above - not native out-of-the-box | €217.05 - €243.10 (conv. from $)
Heating | H-1b / H-1c / H-1d / C-1b / C-1c | Heat/cool generator + distribution control, TABS emission control | Air-to-water heat pump (monobloc/split) with intelligent controller | Bosch | Compress 7000i AW (CS7000iAW, various kW: 5-17) | 1 - 2 (H-1c/H-1d) up to 2 - 3 (H-1b/C-1b with HPC410) | H-1c L1 - L2 outdoor-compensated/demand-based flow control / H-1d L2 - L3 pump staging / H-1b/C-1b L2 advanced central automatic control (TABS-compatible) | Unit only: est. €6,000 - €11,000 depending on kW size; installed cost typically €13,000 - €20,000+ in the EU | COP up to 5.31 (A7/W35), modulating inverter compressor, reversible (heating+cooling), HPC410 intelligent controller, multiple heating-circuit and solar-integration support | HPC410 controller: Modbus/EMS bus (Bosch EasyControl / Home Connect app); Bosch also offers a KNX/Modbus gateway accessory for BMS integration | EasyControl room unit for zone control; Modbus/KNX gateway for BACS integration; buffer/DHW cylinder for full DHW-1b operation | HPC410 controller natively performs outdoor-temperature-compensated and demand-based flow control (H-1c) and multi-stage pump control (H-1d); TABS/advanced automatic control (H-1b/C-1b) is achievable when configured for underfloor/TABS emission circuits, which the controller explicitly supports. | https://proheat.ee/en/heat-pumps/air-source-heat-pumps/bosch-compress-7000i-aw-air-to-water-heat-pump-without-built-in-boiler-7-kw-r410a-three-phase-400-v | Cross-check vs user-supplied sheet: user's €1,359 figure is far below any plausible unit or installed heat-pump price - almost certainly reflects only the HPC410 controller/accessory line item within a larger BOQ, not the heat pump itself. Flagging this as a likely BOQ line-item price, not full equipment cost. | €6,000 - €11,000
Heating | H-1b / H-1c / H-2b / DHW-1b / C-2a / C-2b | District heating substation control | Communicating district heating controller | Siemens | RVD250-A (Synco heating controller, LPB + M-Bus) | 2 - 3 | L2 demand-based distribution control / L3 variable heat-pump-style generator control depending on load (via LPB-networked generators) | POR - not publicly listed (Siemens Industry Mall, login required); comparable Siemens Synco-series controllers retail €300 - €700 | 28 pre-programmed plant types, 1 heating circuit + DHW, LPB (Local Process Bus) + M-Bus communication, AC 230V | LPB (Siemens proprietary, multi-controller networking) + M-Bus for metering integration; OZW central web gateway for remote/BACS access | OZW772 (or similar) LPB-to-web/BACnet gateway for building-level supervision | LPB networking lets multiple RVD250-A units (and connected heat generators) share load, priority and efficiency data - the mechanism behind demand-based (L2) and, once bridged to a BACS via the OZW gateway, external-signal-aware (L3) generator control. | https://hit.sbt.siemens.com/RWD/app.aspx?module=Catalog&action=ShowProduct&key=S55370-C125 | Cross-check vs user-supplied sheet: the user's sheet lists TWO different 'Siemens RVD250-A' rows with different prices (€9,109 and €3,677) and different service sets - internally inconsistent. Given Siemens does not publish list prices, both figures are almost certainly bundled installation/project totals rather than per-unit equipment cost; do not treat either as a reliable unit price without the underlying quote. | €300 - €700
Heating | H-3 / DHW-3 / C-3 | Heat/cooling energy sub-metering | Ultrasonic heat/cooling energy meter | Siemens | UH50-A74-00 (Qp = 40 m³/h, mounting length 300mm) | 3 - 4 | Central/remote reporting of current + historical performance KPIs, extendable to forecasting/benchmarking via data collector software | POR (Siemens Industry Mall, login-gated); comparable Siemens UH50 sizes retail €400 - €1,200 depending on Qp/DN size | Static ultrasonic flow measurement (no moving parts - high long-term stability), platinum-resistance flow/return sensors, optical + wM-Bus/Modbus/BACnet/LoRaWAN communication modules (ordered separately), EN 1434 class 2 accuracy | Optical interface (local) + wM-Bus/Modbus/BACnet/LoRaWAN comms modules (WZU-series, sold separately) → BMS/metering platform | WZU communication module (choose per project: wM-Bus 868MHz, Modbus, BACnet, or LoRaWAN) + UltraAssist configuration software | Delivers monthly/daily logged consumption values and error/fault flags out of the box (supports L2 - L3 KPI + historical reporting); pairing with a benchmarking/analytics platform on top of the WZU data feed reaches the L4 'forecasting and predictive management' definition. | https://hit.sbt.siemens.com/RWD/app.aspx?rc=NO&lang=en&module=Catalog&action=ShowProduct&key=LYU%3AUH50.. | Cross-check vs user-supplied sheet: user's €5,436 is plausible only as a multi-meter site installation (several meters + comms infrastructure + commissioning), not a single meter - typical single UH50 unit cost is a fraction of that | €400 - €1,200
Heating | H-2a / H-2d | Heat generator control (non-heat-pump) + sequencing | Gas condensing boiler with modulating burner | Viessmann | Vitodens 200-W (B2HB, 3.2-35 kW) | 1 - 2 | L1 variable temp control depending on outdoor temp / L2 variable control depending on load (modulating burner) | Est. €2,500 - €6,000 (unit only) - not independently confirmed against a specific distributor quote | Modulating condensing burner (up to 98% efficiency), weather-compensated control via Vitotronic, cascade-capable (up to 4 boilers via LON) | LON (Vitotronic cascade bus) or Vitocomfort/KNX/Modbus gateway for BMS integration | Vitotronic 300 cascade controller for multi-boiler sequencing; LON-BACnet gateway for BMS visibility | Modulating burner gives continuous load-following output (L2); cascading multiple units via the LON bus and a dynamic-priority cascade controller is what would satisfy H-2d's higher sequencing levels, not the boiler alone. | https://www.viessmann.ie | Price not independently confirmed - flagged as catalogue-indicative, not a distributor quote. Included to fill a genuine gap: the database previously had no gas boiler despite it remaining the dominant EU heat generator. | €2,500 - €6,000
Lighting | L-1a | Occupancy control for indoor lighting | Wireless occupancy/vacancy sensor | Lutron | Radio Powr Savr (ceiling/wall, PIR) | 2 - 3 | Automatic detection auto on/off or dimmed (L2) / manual-on auto-off (L3) | $80 - $130 per sensor | PIR motion sensing, ClearConnect RF wireless, battery or line-powered variants, adjustable timeout | Lutron ClearConnect RF → Vive Hub or Athena system | Vive Wireless Hub or Athena Edge Node for BACnet integration into BMS | Auto-on/off (or auto-dim) on detection is the literal Level 2/3 definition; configuration (manual-on vs auto-on) determines whether it lands at L2 or L3. | https://commercial.lutron.com/us/en/sensors/occupancy-vacancy/wireless-radio-powr-savr |  | €69.46 - €112.87 (conv. from $)
Lighting | L-2 | Daylight-based lighting control | Photosensor / daylight sensor + DALI dimming | Lutron | Radio Powr Savr Daylight Sensor + PowPak DALI module | 3 | Automatic dimming | Daylight sensor ~$90 - $150; PowPak DALI module ~$250 - $400 | Continuous daylight measurement, closed-loop dimming algorithm, DALI/0-10V output | ClearConnect RF sensor → PowPak DALI module → DALI luminaires | DALI-compatible luminaires/ballasts | Continuously trims artificial light output to maintain a target lux level as daylight varies - matches the Level 3 'automatic dimming' definition exactly. | https://assets.lutron.com/a/documents/3685509ea_conferenceroom_scenes_marshallingbox.pdf | Level 4 (scene-based, CCT-tunable) needs a tunable-white DALI-2 luminaire + Lutron Athena/Vive scene engine | €78.14 - €130.23 (conv. from $)
Lighting | L-1a / L-2 | Room-level lighting control power pack | DALI power pack with integrated presence + daylight | EPV Electronics | ecos PM/24V DALI power pack + sensors | 2 - 3 | Automatic detection (L1a) + automatic dimming/switching (L2) | POR (typ. €150 - €300 per power pack + €60 - €120 per sensor) | DALI broadcast/addressable output, up to 30 slave sensors pluggable, constant-light-level algorithm | DALI bus → DALI-BACnet/KNX gateway for BMS-level reporting | DALI-BACnet gateway for central M&C visibility | Combines presence detection and closed-loop daylight dimming to hold a set lux target while switching off when unoccupied - directly implements the L-1a/L-2 combined use-case described in the SRI methodology's office example. | https://www.epvelectronics.com/en/solution-finder/offices/individual-offices/dali-daylight-dimming/ |  | €150 - €300
Lighting | L-1a / L-2 / DE-2 / MC-9 / MC-30 | Bus-based lighting, shading and cross-domain control system | Lighting/HVAC/shading control bus (DIN-rail + wall modules) | Schneider Electric (Clipsal) | C-Bus (dimmer modules, relays, sensor inputs, Wiser gateway) | 2 - 3 | L-1a L2 - L3 automatic detection with BACS communication / L-2 L3 automatic dimming / MC-30 L2 - 3 coordinated multi-TBS platform | 8-channel DIN dimmer (L5508D1D) ~$249 - $400; PIR/presence sensor inputs, relays, and Wiser gateway priced per-component, typically $150 - $600 each | Two-wire C-Bus data cable, distributed intelligence (each device has its own microprocessor), PC-based 'Toolbox' programming, BACnet/DALI/OPC gateways available | C-Bus 2-wire data bus; BACnet Gateway (CT-BACnet) or DALI Gateway accessory for cross-system/BMS integration | C-Bus BACnet Gateway for BMS visibility; Wiser app/touchscreen for scene and schedule programming | Distributed C-Bus intelligence natively coordinates lighting, blinds and (via relay outputs) HVAC interlocks from one logic system - matching L-1a/L-2's automatic-detection-and-dimming definitions and MC-30's 'coordination between TBS', once the optional BACnet gateway exposes it to a wider BMS. | https://www.clipsal.com/clipsal-c-bus | Cross-check vs user-supplied sheet: user's €1,051 and €5,450 figures read as small-vs-larger project bundles (channel count, sensor count, gateway) rather than a single per-unit price - consistent with C-Bus being sold as a modular multi-component system, not one SKU | €216.19 - €347.29 (conv. from $)
Lighting | H-1a / C-1a / L-1a / L-2 / V-6 | Multi-sensor presence + IEQ detector feeding heating, cooling, lighting and IAQ reporting | KNX presence/IEQ detector | Siemens | UP 258D51 (Presence Detector WIDE, multi-sensor: brightness/temp/humidity/CO2) | 2 - 3 (per domain: L-1a/L-2 up to L3 - 4 with constant-light control; V-6 L1 - L2) | 360° presence detection to 64m² + motion to 400m²; integrated brightness/temp/humidity/CO2 sensors; constant-light-level control with automatic calibration; 3 independent presence outputs | £512.61 excl. VAT (£615.13 incl. VAT) | KNX bus-powered (DC 24V), IP20, ceiling flush-mount, 3 independent outputs, built-in IR receiver, ETS-configurable | KNX TP (twisted pair) bus - native, no gateway needed for KNX-based BMS; requires a KNX-BACnet gateway for non-KNX BACS | KNX-BACnet gateway if the wider BMS is not KNX-native; ETS software + KNX-certified integrator for commissioning | A single device's presence, brightness, temperature, humidity and CO2 outputs can each independently drive lighting (L-1a/L-2 constant-light dimming), heating/cooling occupancy setback (H-1a/C-1a L4 'individual room control with occupancy detection'), and IAQ reporting (V-6) - this is the clearest real-world example of MC-9's 'centralised occupancy detection feeding into several TBS' principle. | https://hken.rs-online.com/web/p/pir-sensors/2878602 | Cross-check vs user-supplied sheet: user's €4,845 for a single sensor is roughly 8x the confirmed RS Components unit price (~€600) - likely a multi-unit order or a bundle with the KNX gateway/ETS commissioning labour, not the per-unit list price | €598.66 (conv. from £)
Monitoring and control | MC-3 / MC-4 / MC-13 / MC-25 / MC-30 | Central BACS controller (primary/room level) | Freely-programmable BACnet automation station | Siemens | Desigo PXC (PXC4/5/7 family) | 3 - 4 | Coordinated multi-TBS control, fault detection, central reporting, smart-grid integration - depends on programming/points integrated | Individual I/O and controller modules e.g. N 545D31 ≈ kr.3,981 (~€345); OCI700.1 interface ≈ $2,469 | BACnet Secure Connect, TX-I/O expansion modules, bio-based plastic housing, Desigo CC front end for supervision | BACnet/IP or MS/TP; Desigo CC for building-wide supervision and analytics | TX-I/O modules per point count; Desigo CC licence for the supervisory/analytics layer | A freely-programmed Desigo PXC station is the physical realisation of 'coordinated demand-side management of multiple TBS' (MC-25 L2) and 'central reporting combining TBS of all domains' (MC-13 L3) once enough domains are wired into it and Desigo CC is deployed. | https://www.siemens.com/en-us/products/desigo/pxc/ | Price is per-controller hardware; full-building licensing/engineering is quoted per project | €2,144 (conv. from $)
Monitoring and control | MC-30 | Single automated multi-TBS control platform | Open BAS controller / IoT automation server | Loxone | Miniserver Gen 2 | 2 - 3 | Single platform allowing manual control of multiple TBS (L1) / automated coordination between TBS (L2) / + optimisation based on occupancy/weather/grid (L3) | €600 - €700 (Miniserver); extension modules €60 - €150 each | Native integration of lighting, shading, HVAC, energy monitoring, weather station input; Loxone Config programming environment | Loxone Tree/Air (proprietary) + KNX/Modbus/DALI/1-Wire gateways; Loxone Cloud for remote/API | Loxone weather station + smart meter/PV inverter integration for grid/weather-aware optimisation (L3) | Out-of-the-box orchestrates heating, shading, and lighting from one logic engine (L2); adding the weather station and PV/grid data inputs enables full occupancy+weather+grid optimisation, the literal MC-30 Level 3 definition. | https://www.loxone.com/enen/shop/ |  | €600 - €700
Monitoring and control | MC-4 | Fault detection with diagnosing functions | Building analytics / fault-detection & diagnostics (FDD) software | Siemens | Building X (Analytics module) | 3 - 4 | Central indication of faults/alarms for all relevant TBS (L2 - L3) / + diagnosing functions (L4) | SaaS subscription, POR (typically priced per connected point/building, quote-based) | Cloud analytics on top of Desigo/3rd-party BACnet data, rule-based + ML fault detection, root-cause diagnostics | Ingests BACnet/MQTT/API data from the BACS layer (e.g. Desigo PXC) into the cloud analytics engine | Underlying BACS (e.g. Desigo PXC) providing the raw point data | Applies automated fault-detection rules across all connected domains and surfaces root-cause diagnostics to FM teams - matches the Level 4 definition 'central indication...including diagnosing functions'. | https://www.siemens.com/en-us/products/desigo/ | Representative of the FDD software category generally (Schneider EcoStruxure Building Advisor and Honeywell Forge are directly comparable alternatives) | N/A (no fixed price / POR)
Monitoring and control | MC-9 | Occupancy detection: connected services | Multi-purpose occupancy sensor feeding several TBS | Lutron | Radio Powr Savr (shared with Lighting L-1a; wired into HVAC/BMS via Vive/Athena) | 2 | Centralised occupancy detection feeding into several TBS (e.g. lighting AND heating) | $80 - $130 per sensor (same hardware as L-1a) | PIR sensing, ClearConnect RF, integratable with Vive Hub → BACnet | ClearConnect RF → Vive Hub → BACnet/IP into BMS for cross-domain use (lighting + HVAC setback) | Vive Hub/Athena system exposing the occupancy point on BACnet to the HVAC controller as well as lighting | The same physical sensor's occupancy state, once exposed on the BACnet integration, can simultaneously drive lighting control and HVAC setback - which is the literal MC-9 Level 2 definition ('centralised...feeds into several TBS'). | https://commercial.lutron.com/us/en/whole-building-systems/athena/athena-system-controls |  | €69.46 - €112.87 (conv. from $)
Monitoring and control | MC-3 / MC-4 / MC-13 / MC-25 / MC-30 | Multi-domain BACS controller | Open IP-native BACnet/IoT controller | Distech Controls | EC-BOS (EC-Net ecosystem) | 2 - 3 | Coordinated multi-TBS DSM (MC-25 L2), central reporting combining multiple domains (MC-13 L2 - 3), depending on points/programming | Est. €600 - €1,200 per controller (project-dependent; not independently confirmed against a distributor quote) | Native BACnet/IP, built-in IoT/edge analytics, EC-gfxProgram graphical programming, open (non-proprietary) architecture positioned as an alternative to closed Siemens/Honeywell/JCI ecosystems | BACnet/IP (native, no gateway needed); integrates directly with Niagara/Tridium and other open BMS front ends | EC-Net or Niagara supervisory software for building-wide dashboards and DSM coordination | Distech's open-architecture positioning is a genuine differentiator from the proprietary Siemens/JCI/Honeywell ecosystems already in this database - relevant where interoperability across vendors (not vendor lock-in) is an EPBD/procurement priority. | https://www.distech-controls.com | Price not independently confirmed against a distributor quote | €600 - €1,200
Monitoring and control | MC-13 / MC-25 / MC-28 / MC-30 | Web/BACnet gateway for Synco-series controllers | LPB-to-web/BACnet communication gateway | Siemens | OZW772.16 | 2 - 3 | Enables remote/central reporting (MC-13) and BACS-level exposure of LPB-networked Synco controllers (RVD, RMU, etc.) for coordinated DSM (MC-25) | Est. €400 - €800 (POR via Siemens Industry Mall; not independently confirmed against a distributor price) | Bridges Siemens LPB (Local Process Bus) networks to web browser access and BACnet/IP, remote monitoring/alarming, multi-controller supervision | LPB (device side) → Ethernet/BACnet IP (building/BMS side) | Required companion for any Siemens RVD250-A or RMU710B-1 deployment that needs BMS-level or remote visibility - neither controller has this built in | This is the missing piece flagged in the round-3 correction: without the OZW772 (or equivalent), an RVD250-A/RMU710B-1 installation has no native web server or BACnet exposure, capping it at local-only operation regardless of how it's programmed. | https://www.siemens.com | Add this as a mandatory companion line item whenever RVD250-A or RMU710B-1 appears in a BOQ intended to reach MC-13/MC-25/MC-30 levels above L1 | €400 - €800
Ventilation | V-1a | Supply air flow control at room level | CO2/VOC demand-control ventilation sensor | Vaisala | GMW90 Series CO2/Temp/RH Transmitter | 3 - 4 | Central demand control based on air-quality sensors (L3) / local demand control with damper regulation (L4) | $300 - $550 per sensor (POR, distributor dependent) | CARBOCAP NDIR CO2 sensor, 0 - 2000/5000 ppm, 4-20mA/0-10V/Modbus output, wall mount | Analogue (0-10V/4-20mA) or Modbus RTU to AHU/room controller | Room-level VAV damper/actuator (e.g. Belimo) to physically regulate local flow - required for L4 | Provides the CO2 signal that a central controller uses for demand-based ventilation (L3); paired with a local Belimo VAV actuator regulating flow to that specific zone, it becomes local demand control (L4). | https://www.vaisala.com/en/products/instruments-sensors-and-other-measurement-devices/instruments-industrial-measurements/gmw80 |  | €260.47 - €477.53 (conv. from $)
Ventilation | V-1a / V-6 | IAQ sensing (compact/wireless) | Compact NDIR CO2 sensor module | Senseair | S12 CO2 (also used embedded in 3rd-party IAQ devices) | 3 | Central demand control based on air quality sensors | OEM module price POR (typ. $20 - $40 in volume; integrated retail devices $80 - $150) | True NDIR CO2, low power, digital (UART/I2C) output, compact form factor | UART/I2C → host device → BACnet/Modbus/Zigbee gateway depending on integrator | Integrator's wireless IAQ puck/hub (e.g. Zigbee/LoRaWAN) for building-wide deployment | Feeds real-time CO2 into demand-controlled-ventilation logic; typically embedded inside a retail wireless IAQ sensor product rather than sold standalone to building owners. | https://senseair.com/product/s12-co2/ |  | €17.36 - €34.73 (conv. from $)
Ventilation | V-1c | Air flow / pressure control at air handler level | VAV terminal unit (compact, communicating) | Belimo | CMBV-xxx VAV-Compact (BACnet MS/TP, Modbus RTU, MP-Bus) | 3 - 4 | L3: automatic flow/pressure control without pressure reset / L4: with pressure reset (VFD systems) | $300 - $800 per unit depending on size/torque | Integrated Δp sensor + damper actuator + VAV controller in one housing, 2 - 10 Nm torque range, BACnet/Modbus/MP-Bus | BACnet MS/TP, Modbus RTU, or MP-Bus to AHU/room controller | AHU VFD fan control for true pressure-reset operation (L4) | Combines sensing + actuation + control logic in one communicating device - satisfies automatic flow control (L3); operating alongside a VFD-controlled supply fan with static-pressure reset achieves L4. | https://www.belimo.com/us/shop/en_US/Systems/Room-Solutions/c/17707-17663 |  | €260.47 - €694.58 (conv. from $)
Ventilation | V-1c | Damper actuator (general purpose, communicating) | Configurable rotary damper actuator | Belimo | GMX24-MFT-T | 2 - 3 | Multi-stage / automatic flow control (application dependent) | ~$745 (per unit) | 20 Nm torque, configurable (0-10V/2-10V/floating point), position feedback | Analogue/floating point; BACnet/Modbus variants available in the GMX/NMX range | AHU controller (e.g. Siemens Desigo or Belimo VAV controller) to issue the control signal | Provides precise, feedback-verified damper positioning that a controller can use to regulate zone airflow - the actuator itself is a Level 2 - 3 enabler depending on the control loop it's wired into. | https://www.belimo.com/us/shop/en_US/Damper-Actuators/c/17704 |  | €646.83 (conv. from $)
Ventilation | V-2c | Heat recovery control | MVHR unit with smart bypass control | Zehnder | ComfoAir Q + ComfoConnect LAN C | 1 - 2 | Modulate/bypass heat recovery based on exhaust sensor (L1) / based on multiple room sensors or predictive control (L2) | €2,500 - €4,500 (unit, capacity dependent); ComfoConnect LAN C ≈€150 | Counter-flow heat exchanger up to 84% efficiency, automatic summer bypass, app/BMS connectivity via LAN C gateway | ComfoConnect LAN C: Modbus TCP / KNX / Home Automation API → BMS | ComfoConnect LAN C gateway for BACS integration | Automatic bypass based on exhaust/outdoor sensors matches L1; adding room CO2/temperature sensors network-wide for predictive bypass control reaches L2. | https://www.zehnder-systems.co.uk/products/mechanical-ventilation-heat-recovery/comfoair-q |  | €2,500 - €4,500
Ventilation | V-6 | Reporting information regarding IAQ | IAQ monitoring dashboard sensor (CO2/VOC/PM/RH) | Aranet / Vaisala | Aranet4 / Vaisala Indigo 200 series | 2 - 3 | Real-time + historical IAQ available to occupants (L2) / + warnings on maintenance/occupant actions (L3) | Aranet4 ~$189; Vaisala Indigo transmitter POR (typ. €400 - €700) | CO2 (NDIR), temperature, RH, (PM optional), local display + cloud history, long battery life | Bluetooth/LoRaWAN (Aranet) or Modbus/BACnet (Vaisala Indigo) → cloud dashboard/BMS | Aranet PRO gateway or BMS integration for building-wide historical dashboards + alerting rules | Cloud history + occupant-visible dashboard satisfies L2; configuring threshold-based alerts (e.g. 'open window' or 'service due') satisfies the L3 definition. | https://aranet.com/products/aranet4/ |  | €400 - €700
Ventilation | H-2d / V-1a / V-1c / V-2c / V-2d / C-1c / C-2a / C-2b / DHW-2b | Universal HVAC/AHU process controller | Freely-configurable universal controller (Synco 700 series) | Siemens | RMU710B-1 (single control loop) | 2 - 4 (application/programming dependent) | Regulates temperature, humidity, pressure, airflow, air quality; supports KNX communication and up to 4 expansion modules for multi-loop/multi-domain control | $954 - $1,590 (surplus/used market, Radwell - NOT an authorised Siemens distributor); new-unit price via Siemens Industry Mall is login-gated (POR) | Synco 700 series, freely configurable control loop, KNX communication port, RMZ78x/RMZ79x plug-in expansion & operator modules, 26-language menu | KNX (native); RMZ792 module adds KNX connection for control unit; expansion modules RMZ785/787/788 for extra I/O | RMZ790/791/792 operator/control units; KNX-BACnet gateway if integrating into a non-KNX BMS | Because it is a freely-programmable universal controller (not a fixed-function device), the SRI level it delivers is set entirely by how it's configured: e.g. programmed for VAV pressure-reset control it satisfies V-1c L3 - 4; programmed with sequencing logic across multiple cooling generators it satisfies C-2b L3 - 4. This flexibility is why the user's sheet maps it to 10 different services - that is a legitimate but application-specific claim, not an inherent property of the hardware. | https://www.radwell.com/en-US/Buy/SIEMENS/SIEMENS/RMU710B-1 | Cross-check vs user-supplied sheet: user's €8,721 is far above both the surplus-market price found ($954 - $1,590 ≈ €880 - €1,460) and any plausible single-unit Siemens list price for this controller class - almost certainly a full engineered BMS package (controller + I/O modules + panel + commissioning), not the controller alone. Treat the user's figure as a project cost, not a unit price. CORRECTION (round 3): a subsequent reference sheet described this controller as having a built-in 'web server' - per Siemens' own documentation this is incorrect. The RMU710B-1 is a single-loop KNX controller with NO native web server; remote/web access requires an add-on gateway (e.g. Siemens OZW772). Any BOQ or spec citing 'RMU710B-1 web server' should add the OZW772 (or equivalent) as a separate line item. | €828.29 - €1,380 (conv. from $)
Ventilation | V-1c / V-2c | Air flow/pressure control + heat recovery control (AHU-integrated) | Compact air handling unit with rotary/counterflow heat recovery | Swegon | GOLD RX (compact AHU, up to 85% heat recovery) | 3 - 4 (V-1c) / 1 - 2 (V-2c) | V-1c: automatic flow/pressure control, with or without pressure reset depending on fan configuration / V-2c: modulating bypass based on exhaust/multiple sensors | Est. €10,000 - €80,000 depending on airflow capacity (0.1 - 10 m³/s) - not independently price-confirmed against a distributor quote | EC (electronically commutated) fans, rotary or counterflow heat exchanger up to 85% thermal efficiency, integrated Compact Control Unit with BACnet/Modbus/LON | Native BACnet/Modbus/LON via Swegon Compact Control (CC) unit | Building-level BMS integration via the AHU's native BACnet/Modbus port | Integrated EC fans with pressure sensors give automatic flow/pressure control (V-1c L3 - 4 depending on reset strategy); the heat-recovery bypass modulates based on exhaust-air sensors as standard, with multi-sensor/predictive bypass achievable via BMS-level programming (V-2c L1 - L2). | https://www.swegon.com | Price range is a rough capacity-based estimate, not a confirmed quote - AHUs of this type are inherently project-specific/custom-configured | €10,000 - €80,000
Ventilation | V-2d | Supply air temperature control at the air handling unit level (sensing input) | Duct-mounted temperature sensor | Belimo | 22DT (duct temperature sensor) | Enabling component for V-2d L1 - L3 depending on the controller it feeds | Provides the raw supply-air-temperature signal a controller uses for constant-setpoint, outdoor-compensated, or load-dependent control | Est. €80 - €150 (not independently confirmed against a distributor quote) | Duct-mount NTC/Pt1000 sensing element, 0-10V or passive resistance output | 0-10V analogue or passive resistance → AHU controller (e.g. Belimo VAV unit or Siemens RMU710B-1) | An AHU/VAV controller (this sensor has no control logic of its own) | As with other basic sensors in this database, the functionality level V-2d actually reaches is set entirely by the controller and setpoint strategy this sensor feeds, not by the sensor itself. | https://www.belimo.com | Price not independently confirmed against a distributor quote | €80 - €150