## Table 1
Domain Domestic hot water
| code | service | 1
| DHW-1a | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) |  | Service group: Control DHW production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Automatic control on / off | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control on / off and scheduled charging enable | 1 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | Automatic control on / off and scheduled charging enable and multi- sensor storage management | 2 | 2 | 0 | 2 | 0 | 0 | 0
| level 3 | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) | 2 | 3 | 0 | 2 | 0 | 0 | 0
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 1
| DHW-1b | Control of DHW storage charging (using hot water generation) |  | Service group: Control DHW production facilities
IMPACTS
| Functionality levels |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Automatic control on / off | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control on / off and scheduled charging enable | 1 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management | 2 | 2 | 0 | 2 | 0 | 0 | 0
| level 3 | DHW production system capable of automatic charging control based on external signals (e.g. from district heating grid) | 2 | 3 | 0 | 2 | 0 | 0 | 0
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 0
| DHW-1d | Control of DHW storage charging (with solar collector and supplymentary heat generation) |  | Service group: Control DHW production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Manual selected control of solar energy or heat generation | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge | 1 | 0 | 0 | 1 | 0 | 0 | 0
| level 2 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management | 2 | 1 | 0 | 2 | 0 | 0 | 0
| level 3 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management | 3 | 2 | 0 | 2 | 0 | 0 | 0
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 0
| DHW-2b | Sequencing in case of different DHW generators | Service group: Control DHW production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Priorities only based on running time | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Control according to fixed priority list: e.g. based on rated energy efficiency | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | 3 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | 3 | 3 | 0 | 0 | 0 | 0 | 0
Information sources Standard?
| code | service | 1
| DHW-3 | Report information regarding domestic hot water performance | Service group: Information to occupants and facility managers
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Indication of actual values (e.g. temperatures, submetering energy usage) | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Actual values and historical data | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Performance evaluation including forecasting and/or benchmarking | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 0 | 0 | 1 | 0 | 2 | 3
Information sources Standard?