## Table 1
Domain Heating
| code | service | 1
| H-1a | Heat emission control |  | Service group: Heat control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control (e.g. central thermostat) | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Individual room control (e.g. thermostatic valves, or electronic controller) | 2 | 0 | 2 | 2 | 2 | 0 | 0
| level 3 | Individual room control with communication between controllers and to BACS | 2 | 0 | 2 | 3 | 2 | 1 | 0
| level 4 | Individual room control with communication and occupancy detection | 3 | 0 | 2 | 3 | 2 | 1 | 0
Information sources Standard?
EN 15232
| code | service | 0
| H-1b | Emission control for TABS (heating mode) |  | Service group: Heat control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Advanced central automatic control | 1 | 0 | 1 | 2 | 2 | 0 | 0
| level 3 | Advanced central automatic control with intermittent operation and/or room temperature feedback control | 2 | 0 | 2 | 3 | 2 | 1 | 1
| level 4 | 0
Information sources
| Standard? |  | EN 15232
| code | service | 1
| H-1c | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | Service group: Heat control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Outside temperature compensated control | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Demand based control | 2 | 0 | 1 | 1 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 0
| H-1d | Control of distribution pumps in networks | Service group: Heat control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On off control | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Multi-Stage control | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | Variable speed pump control (pump unit (internal) estimations) | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | Variable speed pump control (external demand signal) | 2 | 0 | 0 | 0 | 0 | 0 | 0
Information sources Standard?
EN 15232
| code | service | 0
| H-1f | Thermal Energy Storage (TES) for building heating (excluding TABS) | Service group: Heat control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Continuous storage operation | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Time-scheduled storage operation | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Load prediction based storage operation | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Heat storage capable of flexible control through grid signals (e.g. DSM) | 2 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 1
| H-2a | Heat generator control (all except heat pumps) | Service group: Control heat production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Constant temperature control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Variable temperature control depending on outdoor temperature | 1 | 0 | 1 | 0 | 0 | 0 | 0
| level 2 | Variable temperature control depending on the load (e.g. depending on supply water temperature set point) | 2 | 0 | 2 | 0 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 1
| H-2b | Heat generator control (for heat pumps) | Service group: Control heat production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | On/Off-control of heat generator | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors) | 1 | 1 | 1 | 0 | 0 | 0 | 0
| level 2 | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | 2 | 1 | 2 | 0 | 0 | 0 | 0
| level 3 | Variable control of heat generator capacity depending on the load AND external signals from grid | 2 | 3 | 2 | 0 | 0 | 0 | 0
| level 4 | 0
Information sources Standard?
| code | service | 0
| H-2d | Sequencing in case of different heat generators | Service group: Control heat production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Priorities only based on running time | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Control according to fixed priority list: e.g. based on rated energy efficiency | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | 3 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | 3 | 3 | 0 | 0 | 0 | 0 | 0
Information sources Standard?
EN 15232
| code | service | 1
| H-3 | Report information regarding heating system performance | Service group: ormation to occupants and facility manag
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Central or remote reporting of current performance KPIs and historical data | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 0 | 0 | 1 | 0 | 3 | 3
Information sources Standard?
| code | service | 0
| H-4 | Flexibility and grid interaction | Service group: Flexibility and grid interaction
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Scheduled operation of heating system | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Self-learning optimal control of heating system | 2 | 1 | 2 | 2 | 0 | 0 | 0
| level 3 | Heating system capable of flexible control through grid signals (e.g. DSM) | 2 | 3 | 2 | 3 | 0 | 0 | 0
| level 4 | Optimized control of heating system based on local predictions and grid signals (e.g. through model predictive control) | 2 | 3 | 3 | 3 | 1 | 0 | 0