## Table 1
Domain Ventilation
| code | service | 1
| V-1a | Supply air flow control at the room level |  | Service group: Air flow control
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No ventilation system or manual control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Clock control | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Occupancy detection control | 1 | 0 | 2 | 2 | 2 | 0 | 0
| level 3 | Central Demand Control based on air quality sensors (CO2, VOC, humidity, ...) | 2 | 0 | 3 | 3 | 3 | 0 | 0
| level 4 | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers | 3 | 0 | 3 | 3 | 3 | 0 | 0
Information sources Standard?
EN 15232
| code | service | 0
| V-1c | Air flow or pressure control at the air handler level |  | Service group: Air flow control
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control: Continuously supplies of air flow for a maximum load of all rooms | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On off time control: Continuously supplies of air flow for a maximum load of all rooms during nominal occupancy time | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Multi-stage control: To reduce the auxiliary energy demand of the fan | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | Automatic flow or pressure control without pressure reset: Load dependent supplies of air flow for the demand of all connected rooms. | 3 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | Automatic flow or pressure control with pressure reset: Load dependent supplies of air flow for the demand of all connected rooms (for variable air volume systems with VFD). | 3 | 0 | 0 | 0 | 0 | 0 | 0
Information sources Standard?
EN 15232
| code | service | 0
| V-2c | Heat recovery control: prevention of overheating |  | Service group: Air temperature control
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Without overheating control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Modulate or bypass heat recovery based on sensors in air exhaust | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control | 2 | 0 | 2 | 2 | 2 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 0
| V-2d | Supply air temperature control at the air handling unit level |  | Service group: Air temperature control
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Constant setpoint: A control loop enables to control the supply air temperature, the setpoint is constant and can only be modified by a manual action | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Variable set point with outdoor temperature compensation | 2 | 0 | 2 | 1 | 0 | 0 | 0
| level 3 | Variable set point with load dependant compensation. A control loop enables to control the supply air temperature. The setpoint is defined as a function of the loads in the room | 3 | 0 | 2 | 1 | 0 | 0 | 0
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 0
| V-3 | Free cooling with mechanical ventilation system | Service group: Free cooling
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Night cooling | 1 | 0 | 3 | 2 | 1 | 0 | 0
| level 2 | Free cooling: air flows modulated during all periods of time to minimize the amount of mechanical cooling | 2 | 0 | 3 | 2 | 1 | 0 | 0
| level 3 | H,x- directed control: The amount of outside air and recirculation air are modulated during all periods of time to minimize the amount of mechanical cooling. Calculation is performed on the basis of temperatures and humidity | 3 | 0 | 3 | 2 | 1 | 0 | 0
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 1
| V-6 | Reporting information regarding IAQ | Service group: Feedback - Reporting information
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Air quality sensors (e.g. CO2) and real time autonomous monitoring | 0 | 0 | 0 | 0 | 2 | 1 | 1
| level 2 | Real time monitoring & historical information of IAQ available to occupants | 0 | 0 | 0 | 0 | 3 | 1 | 2
| level 3 | Real time monitoring & historical information of IAQ available to occupants + warning on maintenance needs or occupant actions (e.g. window opening) | 0 | 0 | 0 | 0 | 3 | 2 | 3
| level 4 | 0
Information sources Standard?