## Table 1
Domain Cooling
| code | service | 1
| C-1a | Cooling emission control |  | Service group: Cooling control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Individual room control | 1 | 0 | 1 | 2 | 2 | 0 | 0
| level 3 | Individual room control with communication between controllers and to BACS | 2 | 0 | 2 | 3 | 2 | 1 | 0
| level 4 | Individual room control with communication and occupancy detection | 3 | 0 | 2 | 3 | 2 | 1 | 0
Information sources Standard?
EN 15232
| code | service | 0
| C-1b | Emission control for TABS (cooling mode) |  | Service group: Cooling control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Advanced central automatic control | 1 | 0 | 1 | 1 | 2 | 0 | 0
| level 3 | Advanced central automatic control with intermittent operation and/or room temperature feedback control | 2 | 0 | 2 | 3 | 2 | 1 | 1
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 0
| C-1c | Control of distribution network chilled water temperature (supply or return) |  | Service group: Cooling control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Constant temperature control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Outside temperature compensated control | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Demand based control | 2 | 0 | 1 | 1 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 0
| C-1d | Control of distribution pumps in networks | Service group: Cooling control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On off control | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Multi-Stage control | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | Variable speed pump control (pump unit (internal) estimations) | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | Variable speed pump control (external demand signal) | 2 | 0 | 0 | 0 | 0 | 0 | 0
Information sources Standard?
EN 15232
| code | service | 0
| C-1f | Interlock: avoiding simultaneous heating and cooling in the same room | Service group: Cooling control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No interlock | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Partial interlock (minimising risk of simultanieus heating and cooling e.g. by sliding setpoints) | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Total interlock (control system ensures no simultaneous heating and cooling can take place) | 3 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 0
| C-1g | Control of Thermal Energy Storage (TES) operation | Service group: Cooling control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Continuous storage operation | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Time-scheduled storage operation | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Load prediction based storage operation | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Cold storage capable of flexible control through grid signals (e.g. DSM) | 2 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 1
| C-2a | Generator control for cooling | Service group: Control cooling production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | On/Off-control of cooling production | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Multi-stage control of cooling production capacity depending on the load or demand (e.g. on/off of several compressors) | 1 | 1 | 1 | 0 | 0 | 0 | 0
| level 2 | Variable control of cooling production capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | 2 | 1 | 2 | 0 | 0 | 0 | 0
| level 3 | Variable control of cooling production capacity depending on the load AND external signals from grid | 2 | 3 | 2 | 0 | 0 | 0 | 0
| level 4 | 0
Information sources Standard?
EN 15232
| code | service | 0
| C-2b | Sequencing of different cooling generators |  | Service group: Control cooling production facilities
IMPACTS
| Functionality levels |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | Priorities only based on running times | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Fixed sequencing based on loads only: e.g. depending on the generators characteristics such as absorption chiller vs. centrifugal chiller | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Dynamic priorities based on generator efficiency and characteristics (e.g. availability of free cooling) | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Load prediction based sequencing: the sequence is based on e.g. COP and available power of a device and the predicted required power | 3 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | Sequencing based on dynamic priority list, including external signals from grid | 3 | 3 | 0 | 0 | 0 | 0 | 0
Information sources Standard?
EN 15232
| code | service | 1
| C-3 | Report information regarding cooling system performance |  | Service group: Information to occupants and facility managers
IMPACTS
| Functionality levels |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Central or remote reporting of current performance KPIs and historical data | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 0 | 0 | 1 | 0 | 3 | 3
Information sources Standard?
| code | service | 1
| C-4 | Flexibility and grid interaction | Service group: Flexibility and grid interaction
| Functionality levels |  | IMPACTS
|  |  | Energy efficiency | Energy flexibility and storage | Comfort | Convenience | Health, well-being and accessibility | Maintenance and fault prediction | Information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Scheduled operation of cooling system | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Self-learning optimal control of cooling system | 2 | 1 | 2 | 2 | 0 | 0 | 0
| level 3 | Cooling system capable of flexible control through grid signals (e.g. DSM) | 2 | 3 | 2 | 3 | 0 | 0 | 0
| level 4 | Optimized control of cooling system based on local predictions and grid signals (e.g. through model predictive control) | 2 | 3 | 3 | 3 | 1 | 0 | 0
Information sources Standard?